Sallisaw Casino

HVAC Server Room Project Scope of Work

- Furnish and install A/C package unit as a redundant A/C system for the Sallisaw server room per Drawings, prints, and specifications.

- Bids are to be broken down per category of work, i.e. equipment, HVAC, electric, fence, concrete, etc. Separate costs for materials and labor per category.

- Must provide a list of subcontractors with bid.

- Must provide a job foreman for project who will be onsite for duration of project.

- Controls will be responsibility of CNE but will need to be coordinated with HVAC vendor.

- All work shall be performed in accordance with the latest adopted editions of the applicable International Building Code (“IBC”), Uniform Mechanical Code (“UMC”), Uniform Plumbing Code (“UPC”), National Electric Code (“NEC”) and all other applicable Federal, State and local regulations.

- The word “Provide” means; furnish, install and connect all accessories and ancillary equipment for a complete and operable installation.

- Existing conditions: The drawings indicate new work to be performed and does not purport to show all existing conditions. Contractor shall visit the site prior to bid and familiarize himself with all existing and proposed conditions which may affect the course of work. Contractor shall report all discrepancies and unacceptable conditions to Engineer and Owner prior to bid. No change orders will be allowed for failure to comply with this requirement.

- Contractor shall pay for all fees and obtaining all permits and inspections required for this project.

- Submittals: Contractor will be required to submit eight (8) copies of all Electrical factory shop drawings for all new lighting fixtures, switchgear, panels, motor controls, wiring devices, etc. proposed for this project. Proposed substitutions shall be equal or superior to specified items in all respects. Determination of equality rests solely with the Engineer. Contractor will be required to submit five (5) copies of all Mechanical shop drawings and technical data sheets for all equipment and materials specified herein to the Engineer. The Engineer shall review shop drawings and technical data sheets for conformance with the contract documents and issue a written assessment to the owner prior to commencement of work. The Contractor shall be responsible for all Engineering fees necessary to change permit documents based on alternate submittal packages/equipment substitutions.

- All substitutions shall be submitted to the Engineer prior to bidding. The Owner’s representative shall preapprove any proposed substitution in writing. The Contractor shall be responsible for coordinating all requirements associated with substituted equipment or materials with other building trades, including all electrical, structural, or architectural elements. The Contractor shall identify and annotate all revised requirements per building trade on the shop drawings. The Contractor shall also identify all cost debits or credits in writing for the proposed changes per building trade.

- Upon completion of construction, the Contractor shall supply the Engineer with five (5) complete sets of as-built documents accurately showing the materials and equipment as installed.

- All materials and workmanship shall be guaranteed for a minimum of one (1) year from date of acceptance by owner. Refrigeration compressors shall be guaranteed for a minimum of five (5) years from date of owner’s acceptance. In addition, the Contractor shall guarantee that the installation when operated in accordance with the contractor’s instructions will develop capacity and characteristics as specified and will fulfill each and every requirement of the drawings and specifications. Should the installation in any way fail to do so, the contractor will, without delay or without cost to the owner, provide whatever additional equipment, material, and labor required to correct the deficiency and comply with the requirements of the drawing and specifications.

- Contractor shall check and verify all sizes, dimensions, and conditions before starting any work. Any deviation or problems shall be transmitted to the Engineer for review.

- It is the Contractor’s responsibility to read and review all drawing notes and specifications and to completely understand responsibilities associated with this project. All RFI’s are to be submitted in writing only, nothing verbal, to CNE Buyer, Matt Williams @ matthew.williams@cnent.com.