SCOPE OF WORK

AXIS IP Camera Replacement Program

Replacement of 77 existing AXIS devices with current-generation, TLS 1.3-capable equipment

# 1. Project Overview

The project consists of furnishing, removing, installing, configuring, testing, and commissioning 77 replacement AXIS network video devices identified in the supplied equipment lists. The objective is to replace the identified legacy cameras with current AXIS models while maintaining or improving intended coverage, form factor, operating environment, and security capabilities.

# 2. Scope of Work

Verify existing camera locations, mounting conditions, cable pathways, network connectivity, and PoE availability before replacement.

Provide and install 77 replacement AXIS devices in accordance with the procurement schedule.

Remove the identified legacy devices and associated replacement hardware while protecting suitable existing infrastructure.

Install replacement devices using existing mounting locations and pathways where compatible; provide required mounting adapters and installation accessories. If current mounts can be reused, then reuse them.

Connect each replacement device to the existing IP video/security network and applicable VMS/management platform.

Apply approved device naming, IP addressing, credentials, time/NTP settings, firmware/AXIS OS settings, and site-standard configuration parameters supplied by the Owner.

Enable and validate HTTPS/TLS 1.3 capability and apply the Owner's approved cybersecurity configuration baseline.

Configure image settings, field of view, focus/zoom where applicable, IR settings, and applicable analytics to match intended coverage.

Configure panoramic, multidirectional, PTZ, and intercom functions where applicable.

Perform functional testing of video, power, network communications, recording, live view, image quality, camera controls, and applicable events.

Confirm each installed device is visible and operational in the designated VMS/recording platform.

Label installed devices and document final location, model, serial number, IP address, and configuration information.

Remove replaced equipment from the work area and dispose of or return it per Owner direction.

# 3. Equipment Replacement Schedule

The following schedule is based on the supplied existing-camera inventory and replacement mapping. Quantities total 106 devices.

| Existing Model | Qty | Replacement Model | US Part No. | Resolution | Form Factor | Environment | IR |
| --- | --- | --- | --- | --- | --- | --- | --- |
| AXIS M3203 | 15 | AXIS P3275-V | 03501-001 | 1920x1080 (2 MP) | Fixed dome | Indoor | No |
| AXIS M3047-P | 33 | AXIS M4327-P | 02636-004 | 2160x2160 (4.7 MP) | Panoramic / digital PTZ | Indoor | No |
| AXIS M3007 | 1 | AXIS M4327-P | 02636-004 | 2160x2160 (4.7 MP) | Panoramic / digital PTZ | Indoor | No |
| AXIS Q3505 Mk II | 6 | AXIS Q3546-LVE 10 mm | 02971-001 | 2688x1512 (4 MP) | Fixed dome | Outdoor | Yes |
| AXIS P3225-LVE Mk II | 5 | AXIS P3275-LVE 10 mm | 03150-001 | 1920x1080 (2 MP) | Fixed dome | Outdoor | Yes |
| AXIS M3114 | 4 | AXIS M3215-LVE | 02371-001 | 1920x1080 (2 MP) | Fixed dome | Outdoor | Yes |
| AXIS M2026-LE Mk II | 4 | AXIS M2036-LE | 02125-001 | 2304x1728 (4 MP) | Fixed bullet | Outdoor | Yes |
| AXIS M3113 | 3 | AXIS M3215-LVE | 02371-001 | 1920x1080 (2 MP) | Fixed dome | Outdoor | Yes |
| AXIS P3707-PE | 3 | AXIS P3735-PLE | 02633-001 | 4 x 1920x1080 | 4-sensor multidirectional | Outdoor | Yes |
| AXIS P9106-V | 1 | AXIS P9117-PV | 02864-001 | 2160x2160 (6 MP) | Corner / panoramic | Indoor | No |
| AXIS P3225-LV Mk II | 1 | AXIS P3275-LV | 03149-001 | 1920x1080 (2 MP) | Fixed dome | Indoor | Yes |
| AXIS P3364 | 1 | AXIS P3275-V | 03501-001 | 1920x1080 (2 MP) | Fixed dome | Indoor | No |
| AXIS A8105-E | 1 | AXIS I8116-E White | 02408-001 | 2592x1944 (5 MP) | Network video intercom | Outdoor | No |

Total existing devices: 77   Total replacement devices: 77

# 4. Procurement Bill of Materials

| Replacement Model | US Part Number | Qty | Resolution | Environment |
| --- | --- | --- | --- | --- |
| AXIS I8116-E White | 02408-001 | 1 | 2592x1944 (5 MP) | Outdoor |
| AXIS M2036-LE | 02125-001 | 4 | 2304x1728 (4 MP) | Outdoor |
| AXIS M4327-P | 02636-004 | 33 | 2160x2160 (4.7 MP) | Indoor |
| AXIS P3275-LV | 03149-001 | 1 | 1920x1080 (2 MP) | Indoor |
| AXIS P3275-LVE 10 mm | 03150-001 | 5 | 1920x1080 (2 MP) | Outdoor |
| AXIS P3275-V | 03501-001 | 16 | 1920x1080 (2 MP) | Indoor |
| AXIS M3215-LVE | 02371-001 | 7 | 1920x1080 (2 MP) | Outdoor |
| AXIS P3735-PLE | 02633-001 | 3 | 4 x 1920x1080 | Outdoor |
| AXIS P9117-PV | 02864-001 | 1 | 2160x2160 (6 MP) | Indoor |
| AXIS Q3546-LVE 10 mm | 02971-001 | 6 | 2688x1512 (4 MP) | Outdoor |

# 5. Installation and Configuration Requirements

Reuse existing structured cabling where it passes inspection and is compatible with the replacement device. Cabling replacement is a change-order item unless expressly included.

Confirm adequate PoE power and switch capacity before cutover. Network infrastructure upgrades are excluded unless specifically included.

Maintain existing camera coverage to the greatest practical extent. Where field of view or mounting geometry changes, perform final aiming and coverage verification with the Owner.

Coordinate camera outages with the Owner and replace devices in a controlled sequence to minimize surveillance downtime.

Use Owner-approved credentials and cybersecurity standards; no default passwords shall remain in production.

Update device firmware/AXIS OS to the Owner-approved release, subject to VMS compatibility.

Configure HTTPS and validate TLS 1.3 support. The supplied AXIS OS source note states that AXIS OS supports TLS 1.2 and TLS 1.3 cipher suites for HTTPS.

Installer must have the following certifications:

MCDE (Milestone CCTV Certified Design Engineer)

MCIT (Milestone Certified Integration Technician)

Axis Certified Professional (ACP)

# 6. Testing and Acceptance

Verify power, network connectivity, and intended network configuration.

Verify live video in the designated VMS/client.

Verify recording as required by the existing or approved system configuration.

Verify image orientation, focus, exposure, and field of view.

Verify IR operation for applicable models where nighttime operation is required.

Verify PTZ movement, zoom, and presets for the AXIS P5654-E Mk II replacement.

Verify panoramic/multidirectional sensor views for AXIS M4327-P and AXIS P3735-PLE replacements.

Verify video/audio intercom functions for the AXIS I8116-E replacement where applicable.

Verify HTTPS/TLS configuration and document site-specific cybersecurity exceptions.

Correct installation/configuration deficiencies identified during commissioning and obtain Owner sign-off.

# 7. Deliverables

Installed and commissioned replacement devices.

Final device inventory including location, model, serial number, and IP address.

Updated camera/device schedule or as-built location information, as applicable.

Configuration and commissioning checklist documenting test results.

Documentation of approved deviations or field changes.

Basic Owner orientation/training if included in the commercial proposal.

1 year workmanship warranty

# 8. Assumptions

Existing network, PoE, VMS, recording, and storage infrastructure are operational and has sufficient capacity unless identified during site verification.

Existing cable routes and mounting locations can generally be reused.

The Owner will provide network addressing, VLAN information, VMS access, cybersecurity requirements, and authorized credentials.

Work will occur during mutually agreed access windows; after-hours, weekend, lift, traffic-control, or special-access requirements are excluded unless stated in the proposal.

Permits, structural repairs, major electrical work, and fire/life-safety work are excluded unless specifically listed in the contract.

# 9. Exclusions / Potential Change-Order Items

Replacement or remediation of damaged/failed structured cabling.

New network switches, PoE injectors, UPS systems, fiber equipment, or other network infrastructure.

VMS licensing, recording-server upgrades, storage expansion, or third-party software licensing.

Major camera relocation requiring new pathways, coring, trenching, structural reinforcement, or significant electrical work.

Painting, patching, roofing, weatherproofing repairs, or restoration beyond normal minor installation activities.

Third-party system integration not already supported/configured in the existing environment. Excluding the existing Milestone platform.

Correction of pre-existing network, VMS, cybersecurity, or power problems unrelated to camera replacement.

Final pricing, schedule, labor hours, travel, lift/equipment requirements, taxes, freight, disposal fees, and warranty terms should be established in the contractor's commercial proposal. This Scope of Work defines the work content and equipment basis.

# 12. Bid Information

Site Locations:

Marshall/Interchange 10838 East Marshall Street, Tulsa, OK

Prison Museum124 E Choctaw St, Tahlequah, OK

National History Museum 101 S Muskogee Ave, Tahlequah, OK

Cherokee Springs Golf 700 E Ballentine Rd, Tahlequah, OK

Cherokee Trails Golf 22706 S 504 Rd, Tahlequah, OK

Lynn Lane 1021 N Lynn Ln Rd, Catoosa, OK

Sequoyah's Cabin Museum 470288 Hwy 101, Sallisaw, OK

Ani Art Center406 B W Locust St, Stilwell, OK

Bids are due: Monday, November 2, 2026 at 5pm CST

Please email all bids to:  AXIS_IP.sq7zfmsuhg3rxgxt@u.box.com

Email all questions to stephanie.shults@cnbglobal.com no later than Friday, October 23, 2026, at 5pm CST.

BID SHEET / PRICING SCHEDULE

AXIS IP Camera Replacement Program – 77 Devices

Bidders shall complete all applicable pricing fields below. Unless otherwise noted, pricing shall include all labor, supervision, standard installation materials, configuration, testing, commissioning, documentation, and incidental costs necessary to provide a complete and operational installation in accordance with the Scope of Work.

| Item | Replacement Model | AXIS Part No. | Qty | Unit Material | Extended Material | Unit Labor | Extended Labor |
| --- | --- | --- | --- | --- | --- | --- | --- |
| 1 | AXIS I8116-E White | 02408-001 | 1 | $ ______ | $ ______ | $ ______ | $ ______ |
| 2 | AXIS M2066-LE | 02125-001 | 4 | $ ______ | $ ______ | $ ______ | $ ______ |
| 3 | AXIS M4327-P | 02636-004 | 33 | $ ______ | $ ______ | $ ______ | $ ______ |
| 4 | AXIS P3275-LV | 03149-001 | 1 | $ ______ | $ ______ | $ ______ | $ ______ |
| 5 | AXIS P3275-LVE 10mm | 03150-001 | 5 | $ ______ | $ ______ | $ ______ | $ ______ |
| 6 | AXIS P3275-V | 03501-001 | 16 | $ ______ | $ ______ | $ ______ | $ ______ |
| 7 | AXIS M3215-LVE | 02371-001 | 7 | $ ______ | $ ______ | $ ______ | $ ______ |
| 8 | AXIS P3735-PLE | 02633-001 | 3 | $ ______ | $ ______ | $ ______ | $ ______ |
| 9 | AXIS P9117-Pv | 02864-001 | 1 | $ ______ | $ ______ | $ ______ | $ ______ |
| 10 | AXIS Q3546-LVE 10MM | 02971-001 | 6 | $ ______ | $ ______ | $ ______ | $ ______ |
| Equipment & Installation Subtotal |  |  |  | $ ______ | $ ______ | $ ______ | $ ______ |

Note: The bid schedule is intentionally structured for bidder-entered unit pricing. Quantities are based on the supplied replacement equipment schedule and should be reconciled by the bidder before final pricing.

B. General Project Costs

| Item | Description | Qty | Unit Price | Extended Price |
| --- | --- | --- | --- | --- |
| A | Mobilization / demobilization | 1 | $ ______ | $ ______ |
| B | Project management / supervision | 1 | $ ______ | $ ______ |
| C | Site verification / pre-installation survey | 1 | $ ______ | $ ______ |
| D | Camera installation labor – included in equipment schedule or separately priced | 1 | $ ______ | $ ______ |
| E | Configuration, VMS enrollment, and commissioning | 1 | $ ______ | $ ______ |
| F | Testing, documentation, and as-built inventory | 1 | $ ______ | $ ______ |
| G | Removal / disposal of replaced equipment | 1 | $ ______ | $ ______ |
| H | Lift / access equipment, if required | 1 | $ ______ | $ ______ |

C. Optional / Allowance Items

| Item | Description | Allowance Qty | Unit Price | Extended Price |
| --- | --- | --- | --- | --- |
|  | Replacement of existing camera cabling where required | TBD | $ ______ | $ ______ |
|  | New network/PoE equipment, if required | TBD | $ ______ | $ ______ |
|  | New mounting hardware/adapters beyond standard installation | TBD | $ ______ | $ ______ |
|  | Core drilling / pathway work | TBD | $ ______ | $ ______ |
|  | Additional lift or specialty access | TBD | $ ______ | $ ______ |
|  | Other: ______________________________ | TBD | $ ______ | $ ______ |
| CSP – Total Care Option | Provide pricing for a one (1) year comprehensive service agreement, with annual renewal pricing separately identified for Years 2 through 5. Total Care pricing shall include all covered corrective maintenance/break-fix services, troubleshooting, repair support, and semi-annual preventive maintenance and camera cleaning. Vendor shall clearly identify any exclusions, service limitations, response-time commitments, or additional charges not included in the proposed annual price. Vendor to handle all manufactures Warranty/RMAs. | TBD | $ ______ | $ ______ |
| CSP – Break/Fix with Preventive Maintenance Option | Provide pricing for a one (1) year break/fix service agreement, with annual renewal pricing separately identified for Years 2 through 5. Pricing shall include break/fix support and semi-annual preventive maintenance and camera cleaning. Vendor shall clearly identify labor rates, included versus billable services, response-time commitments, minimum charges, and any exclusions or additional costs associated with break/fix services. Vendor to handle all manufactures Warranty/RMAs | TBD | $ ______ | $ ______ |

D. Bid Summary

| Equipment / Camera Replacement | $ __________________ |
| --- | --- |
| Installation Labor | $ __________________ Hours ______ |
| Configuration / Commissioning | $ __________________ Hours ______ |
| General Project Costs | $ __________________ |
| Optional / Allowance Items | $ __________________ |
| Subtotal | $ __________________ |
| Sales Tax | $ __________________ |
| Freight / Shipping | $ __________________ |
| TOTAL BID PRICE | $ __________________ |

E. Bidder Information

Company Name: ________________________________________________

Address: ______________________________________________________

Contact Name: _________________________________________________

Phone: __________________________  Email: __________________________

Bid Valid For: __________________ days

Estimated Lead Time: __________________

Estimated Project Duration: __________________

Warranty: _____________________________________________________

Bidder Signature: ____________________________________    Date: ____________________

Printed Name / Title: ______________________________________________________________