RFP #164856 Questions and Answers-

Q: The state of Oklahoma does not require emergency video/audio communication. Please confirm if this should be included? 
A: ATIS – video/audio communication is an alternate (ALT I). The intent for the base bid is not to include the video portion of the emergency communication. 

Q: Will OEM EVC be acceptable? 

A: ATIS – I would ask for both options – OEM and 3rd party non-proprietary for Alt I. Tag as Alt. 1a. and Alt. 1b.

Q: Will OEM be responsible for monitoring? Or will the owner be responsible for monitoring? 
A: ATIS – Yes and this is included as ALT I (Maint) for the monthly fee associated with monitoring.

Q: Are Columbia car doors acceptable? 
A: ATIS – Yes.

Q: With regards to rebuild/refurbishing machines, has a machine shop or repair company reviewed the scope of work and provided a cost? 
A: ATIS – This is included in the email RFI attached above.

For Tower 2 High Rise Cars 6-9 the specifications indicate one hall station riser per elevator. Please confirm the required quantity of hall station risers for this four-car group. Existing conditions appear to indicate two risers. 
A: ATIS – Yes, please provide 2 risers as per existing.

Q: For Tower 2 Low Rise Cars 1-5 the specifications indicate one hall station riser per elevator. Please confirm the required quantity of hall station risers for this five-car group. Existing conditions appear to indicate two risers.
A: ATIS – Yes, please provide 2 risers as per existing.


Q: The specifications require both emergency power operation and battery lowering. These features are typically mutually exclusive. Do Hydraulic Cars 9 and 10 have building emergency power available?
· If emergency power is available, may battery lowering be omitted?

A: ATIS – Hydraulic (parking) elevators 9 and 10 are not on emergency generator and shall be provided with battery lowering.

Q: Will existing Otis service tool remain on site during interim maintenance?
A: ATIS – No, this is the property of Otis.

Q: Will interim maintenance begin for all elevators once agreement is in place? Or will it be staggered to only take the elevator banks being modernized as they are removed from service?
A: ATIS – Intent is for service to start once material delivery occurs and first elevators (parking elevators) begin modernization.

Q: Has the maintenance spec been created yet and when should we expect to receive it?
A: ATIS – Being issued with this RFI or just before.

Q: Hydraulic Parking Machine Room – Insulation Testing.
A: The existing insulation within the hydraulic parking machine room was requested to be tested to confirm that it does not have asbestos-containing material (ACM).

Q:  Alternate – Existing Machine Refurbishment.
A: For the alternate involving retention and refurbishment of the existing machines, the required refurbishment scope shall, at a minimum, incorporate the recommendations identified in the machine evaluation report included with the RFI documents (attached above). As part of the refurbishment scope, the elevator contractor shall provide documentation from the machine shop verifying the condition of each machine following completion of the refurbishment and confirming that the machine is suitable for 20-30 years of continued service.

Q: Escalator Modernization Sequencing.
A: For bidding and scheduling purposes, both escalators may be removed from service simultaneously. The expectation is that the two escalators will be modernized concurrently to minimize the overall project duration. The contractor shall incorporate this approach into its proposed project schedule, manpower planning, and sequencing.

Q: Contractor Parking.
A: On-site parking will not be provided for contractor personnel. The contractor shall be responsible for arranging off-site parking for all employees, subcontractors, and other personnel associated with the project. All costs associated with parking and transportation to and from the project site shall be included in the contractor’s bid.

Q: After-Hours Work / Building Disruption.
A: The contractor shall plan and coordinate heavy material movement, demolition, and excessively loud or disruptive work to occur after normal building operating hours where reasonably required to minimize disruption and inconvenience to building occupants. The contractor shall coordinate these activities with Building Management in advance.


Q: Protection of Existing Building Finishes.
A: The contractor shall provide adequate protection for all existing floors, walls, doors, corridors, finishes, and other building surfaces affected by material movement or construction activities. The contractor shall maintain work and access areas in a clean condition and prevent damage from dirt, grease, debris, equipment, or material handling. Any damage resulting from the contractor’s work shall be repaired or replaced by the contractor at no additional cost to the Owner.


Q: Tower II Low-Rise – Cherokee Federal Security Requirements — OWNER FEEDBACK REQUIRED.
A: Portions of the work associated with the Tower II low-rise elevators may require access to space occupied by Cherokee Federal. The Owner/Building Management shall provide the specific security and access requirements applicable to contractor personnel entering or working within these areas.


Q: RFI Deadline.
A: All bidder RFIs shall be submitted no later than seven (7) calendar days prior to the bid due date. RFIs received after this deadline may not receive a response prior to the bid due date. Bidders shall account for all issued addenda and RFI responses in their final bid.

Q: TERO — OWNER FEEDBACK / RFP CONFIRMATION REQUIRED.
A: Do we need to provide in an RFI the specific language for the TERO fees or was this already addressed within the RFP/bid documents. Already provided in RFP. 


Q: Sales Tax.
A: Sales tax is applicable to this project. Bidders shall include all applicable sales taxes within their submitted pricing unless specifically identified otherwise in the bid documents.


Q: Applicable Elevator Code.
A: All work shall comply with the currently adopted codes and standards applicable to the project, including the applicable edition of ASME A17.1/CSA B44, Safety Code for Elevators and Escalators, as adopted and amended by the Authority Having Jurisdiction (AHJ), together with all other applicable state and local codes, regulations, and requirements.

